## RFP6 V2 Current Calculation
RFP V2 Series Battery Calculations |  |  |  | Rev | 2 | Date | 2019-11-12
Project:
System Components | Stock Number | No. of Units | Quiescent Current IQ |  | Alarm Current IA |  | Comments
|  |  | mA | Total mA | mA | Total mA
6 Zone Residential Fire Panel | RFP6V2 | 0 | 17 | 0 | 64 | 0 | Select only 0ne panel
12 Zone Residential Fire Panel | RFP12V2 | 0 | 18 | 0 | 80 | 0
18 Zone Residential Fire Panel | RFP18V2 | 0 | 20 | 0 | 95 | 0
Photoelectric Smoke Alarm | EIB650iWX | 0 | 4.5 | 0 | 30 | 0 | Max. 12 Smoke or Heat Alarm per zone
Heat Alarm | EIB603CX | 0 | 6 | 0 | 50 | 0
Roof Space Heat Detector 60⁰ | HS60V2 | 0 | 0 | 0 | 6.7 | 0 | If RIL fitted IA = 14mA
Roof Space Heat Detector 80⁰ | HS60V2 | 0 | 0 | 0 | 6.7 | 0 | If RIL fitted IA = 14mA
Zone tripping card (6 relays) | SUB365A | 0 | 35 | 0 | 125 | 0 | Max. one card for each 6 zones
Total no. of Alarms |  | 0
Ancillary Output |  |  |  | 0 |  | 0
External Strobe Output |  |  |  | 0 |  | 0
VAD |  |  |  | 0 |  | 0
Others |  |  |  | 0 |  | 0
Total current consumption. (mA) |  |  |  | 0 |  | 0
Standby Time (hours) |  | 72
Alarm Time (minutes) |  | 4
Battery Requirement (in AH) |  | 0 |  |  |  |  | Use 7 AH Battery
Nearest Standard Battery Size (A/h) |  | 7
Note: Only yellow cells can be edited